Rockridge Power & Light Company

Meter Testing Program Plan

Document ID: RPL-MTR-PGM-001  |  Version 6.0

| Field | Value |
| --- | --- |
| Document Title | Meter Testing Program Plan |
| Document ID | RPL-MTR-PGM-001 |
| Version | 6.0 |
| Effective Date | 2025-01-13 |
| Approved Date | 2025-01-08 |
| Law As-Of Date | 2024-12-31 |
| Classification | Internal |
| Owner | Gregory Walsh, Manager, Meter Shop & Standards Laboratory |
| Reviewer | Angela Ruiz, Director, Metering |
| Approver | Michael Brennan, Vice President, Operations |
| Supersedes | RPL-MTR-PGM-001 v5.2 (2024-02-05) |

Uncontrolled when printed — verify the current version in DCS before use.

# Table of Contents

1.  Purpose

2.  Scope

3.  Definitions

4.  Regulatory Basis and Industry Standards

5.  Organization and Roles

6.  Meter Records

7.  Meter Location and Accessibility Standards

8.  New and Repaired Meter Acceptance

9.  In-Service Testing Program

10.  Accuracy Limits and Average-Accuracy Method

11.  Test Equipment and Standards

12.  AMI Meter Health Monitoring

13.  Customer-Requested and Commission-Supervised Tests

14.  2024 Program Results (Preliminary)

15.  2025 Test Plan

16.  Program KPIs

17.  Records and Retention

18.  Training and Technician Qualification

19.  Related Documents

20.  Revision History

21.  Approval Block

# 1. Purpose

This Meter Testing Program Plan describes how Rockridge Power & Light Company (RPL) ensures the accuracy, integrity, and regulatory compliance of its meter population. The plan governs new-meter acceptance testing, in-service testing (periodic and statistical sampling), test equipment calibration and traceability, customer-requested testing, and annual program reporting. It applies to all 409,950 revenue meters in RPL's service territory as of 2024-12-31.

# 2. Scope

This plan covers the full RPL revenue meter fleet: 371,200 solid-state AMI meters, 31,400 solid-state AMR meters, and 7,350 electromechanical meters (total: 409,950) within RPL's 14-county service territory in west-central Indiana. Transformer-rated meters (16S, 12S CT-connected) constitute approximately 6,400–8,600 units within the counts above.

# 3. Definitions

As-Found Accuracy: The measured percentage registration of a meter at the time it is removed from service or tested in place, before any adjustment. (170 IAC 4-1-8(a))

Average Accuracy: Arithmetic mean of FL and LL percentage registration: (FL + LL) ÷ 2. (170 IAC 4-1-8(a))

Full Load (FL): Load of approximately 100% of rated test amperes. (170 IAC 4-1-8(a))

Light Load (LL): Load of approximately 10% of rated test amperes. (170 IAC 4-1-8(a))

Homogeneous Group: Subdivision of the in-service meter population with similar operating characteristics. (170 IAC 4-1-10(c)(1))

Lot: Subset of meters within a homogeneous group; minimum 301 meters. (170 IAC 4-1-10(c)(2))

AQL: Acceptable Quality Level for lot testing: 2.50 AQL. (170 IAC 4-1-10(c)(4))

U / L: Upper/Lower Specification Limits for Method B: U = 102%, L = 98%. (170 IAC 4-1-10(c)(5))

Method A: All meters tested on a fixed schedule of not more than 16 years. (170 IAC 4-1-10(b))

Method B: Statistical sampling — annual sample drawn from each homogeneous group lot and tested against the AQL criterion. (170 IAC 4-1-10(c))

# 4. Regulatory Basis and Industry Standards

Indiana Administrative Code 170 IAC 4-1 governs all metering requirements; law as of 2024-12-31. Key sections: §3 (records retention), §4 (test records), §5 (meter location), §6 (new/repaired meter testing), §7 (test equipment), §8 (accuracy method), §9 (accuracy limits), §10 (in-service testing), §11 (customer-requested tests).

ANSI C12.1, ANSI C12.20 referenced as company practice for test procedures and performance requirements. ANSI/ASQC Z1.9-1993 cited in 170 IAC 4-1-10(c)(3); RPL applies an internal sampling plan consistent with its Inspection Level II principles (see §9.3).

# 5. Organization and Roles

Gregory Walsh (P19), Manager, Meter Shop & Standards Laboratory: day-to-day program management, test schedule, equipment calibration, record integrity.

Angela Ruiz (P20), Director, Metering: program ownership, IURC interface, Method B commission notification, annual report approval.

Luis Hernandez (P18), Supervisor, Metering Services: field testing coordination, technician supervision, WAM work order management.

Michael Brennan (P16), Vice President, Operations: approver; informed of annual results and any commission action.

Meter Technicians (MT-### series): 14 certified technicians performing in-service testing (shop and field), new-meter acceptance, and customer tests.

# 6. Meter Records

Whenever any meter in service is tested, a record shall be preserved containing: (1) meter identification; (2) reason for test; (3) pre-test meter reading; and (4) test result with all data necessary to calculate average accuracy. (170 IAC 4-1-4(a))

Permanent records are kept in WAM and include: meter serial, vendor family, technology, form factor, meter class, install date, premise ID, service center, circuit ID, county, group ID, status, last test date, last test reason, and retirement date/reason.

Annual tabulations of test results are prepared by Gregory Walsh (P19) each January for the prior year, ready for IURC submission within 15 calendar days of year-end.

# 7. Meter Location and Accessibility Standards

Meters should be installed outdoors where practical. (170 IAC 4-1-5(A)) RPL's AMI rollout placed 98% of meters in outdoor socket positions.

Mounting height: not less than 4 feet nor more than 6 feet above standing surface, measured from center of meter cover. (170 IAC 4-1-5(B),(C))

Minimum center-to-center spacing on a meter board: 7.5 inches. (170 IAC 4-1-5(C))

Meters shall be easily accessible for reading, testing, and adjustments. (170 IAC 4-1-5(C))

# 8. New and Repaired Meter Acceptance

Each new non-self-contained watthour meter shall be inspected, tested, and adjusted before installation. (170 IAC 4-1-6(a)) Self-contained single-phase meters may rely on certified manufacturer test data; RPL also performs acceptance sampling per §9.3.

Lot formation: each purchase order from a single vendor = one acceptance lot. Minimum lot size for sampling: 25 meters; below 25 = 100% tested.

If acceptance sample fails §9.4 criteria, Gregory Walsh (P19) places the lot on hold, notifies vendor in writing within 5 business days, and initiates return-to-vendor.

All removed meters shall be inspected, cleaned, repaired as necessary, and tested before return to service. (170 IAC 4-1-6(b))

Non-self-contained meters must be tested prior to installation or within 60 days after installation. (170 IAC 4-1-6(c),(d))

# 9. In-Service Testing Program

Meter groups (homogeneous groups) are formed by: technology, vendor family, form factor, meter class, service type, and install-year band. Minimum group size: 301 meters. (170 IAC 4-1-10(c)(2)) RPL maintains 53 active homogeneous groups as of 2024-12-31.

Method B is used for all solid-state (AMI and AMR) self-contained groups. Method A 16-year periodic is used for electromechanical meters and all demand-register classes.

Sample size table (company practice — RPL Meter Sampling Plan, consistent with ANSI/ASQC Z1.9-1993 Inspection Level II principles): lot size 2–8 → n=3; 9–15 → n=4; 16–25 → n=5; 26–50 → n=7; 51–90 → n=10; 91–150 → n=15; 151–280 → n=25; 281–500 → n=35; 501–1200 → n=50; 1201–3200 → n=75; 3201–10000 → n=100; 10001–35000 → n=150; 35001–150000 → n=200; 150001–500000 → n=300.

Lot acceptance uses Double Specification Limit–Variability Unknown–Standard Deviation Method at 2.50 AQL with U=102%, L=98%. (170 IAC 4-1-10(c)(4),(5)) If rejected, accelerated testing is required within a maximum of 96 months. (170 IAC 4-1-10(c)(7))

# 10. Accuracy Limits and Average-Accuracy Method

Average percentage accuracy = (FL + LL) ÷ 2. (170 IAC 4-1-8(a))

Limits: average error ≤ ±2.00%; FL error ≤ ±1.00%; LL error ≤ ±3.00%. (170 IAC 4-1-9(b)(1)(A),(B),(C))

No-load prohibition: no meter that registers more than one revolution at no-load with voltage < 110% of standard service voltage. (170 IAC 4-1-9(a))

Power-factor test for CT-metered installations: tested at 100% rated current, 50% lagging PF; error must not exceed ±2.00%. (170 IAC 4-1-9(b)(5))

Demand register limits: integrating demand — timing element ≤ ±2% for full billing period; TOU register — max 10-minute time error; electromagnetic lagged ≤ ±2% full scale; thermal lagged ≤ ±4% full scale. (170 IAC 4-1-9(b)(3),(4))

# 11. Test Equipment and Standards

Test equipment hierarchy: NIST → Accredited External Laboratory → RPL Reference Standards (3 units) → Shop Test Boards (8 units) → Portable Standards (32 units) → Revenue meters.

Reference standards recalibrated at least every 2 years by a recognized standardizing laboratory. (170 IAC 4-1-7(C))

Portable standards checked before each field campaign. If found in error more than ±1%, immediately taken out of service for recalibration. (170 IAC 4-1-7(D))

All calibration certificates are filed in WAM asset records and physically at the Meter Shop & Standards Laboratory (records series RRS-MTR-003).

# 12. AMI Meter Health Monitoring

Company practice (supplements but does not replace Method B annual sample).

AMI HES continuously collects event data. Flags triggering removal-for-test after 14 consecutive days: zero-consumption, tamper event, power quality disturbance, metrology diagnostic fault, disconnect switch failure.

Analytics engine (company practice) flags meters whose 30-day rolling consumption deviates by more than ±35% from prior 12-month baseline adjusted for degree-days.

# 13. Customer-Requested and Commission-Supervised Tests

Each customer may request a meter accuracy test in writing. First and second tests in any 12-month period are free. (170 IAC 4-1-11(a))

Subsequent tests may be billed if meter was tested within prior 36 months and found in compliance. (170 IAC 4-1-11(b)) Fee (company tariff §1.6): $40.00 residential/single-phase; $95.00 polyphase/demand.

Written test report to customer within 10 days of test completion. (170 IAC 4-1-11(d))

Customer may appeal test result to IURC within 5 days of report date. (170 IAC 4-1-11(e))

# 14. 2024 Program Results (Preliminary)

Data extracted 2025-01-03. Total tests: 5,724 (AMI: 4,303; AMR: 843; EM: 578).

Within-limits rates: AMI 99.73%; AMR 99.76%; EM 95.33%. No group acceptance failure in 2024. EM meters show highest error rate consistent with age profile (1972–2004).

Customer tests: 620. New acceptance lots: per new_meter_lots_2024.csv.

Full test results: data/meter_test_results_2024.csv.

# 15. 2025 Test Plan

Annual sample draw executed by January 15, 2025 by Gregory Walsh (P19). Sample selections documented in data/inservice_sample_selection_2025.csv (3,750 meters selected across 53 groups).

Method A periodic tests scheduled via WAM work order MTR-TST for meters within 60 days of their next-due date. Quarterly distribution of EM periodic tests per population file.

# 16. Program KPIs

Annual sample completion rate ≥ 98% by December 31.

Test report issuance within 10 days for customer tests: 100% compliance.

Reference standard recalibration on schedule: 100%.

No unresolved billing review actions outstanding > 90 days.

# 17. Records and Retention

All meter test records retained for a minimum of 3 years. (170 IAC 4-1-3)

Records kept in Indiana and available for IURC inspection. (170 IAC 4-1-3)

Records series: RRS-MTR-001 (new meter lot records), RRS-MTR-002 (in-service and customer test records), RRS-MTR-003 (calibration certificates).

# 18. Training and Technician Qualification

All meter technicians (MT-### series) hold current AEMC certification or equivalent RPL qualification as verified by Gregory Walsh (P19) annually.

Technicians performing field testing must complete hands-on competency evaluation for portable standard use before each field season.

# 19. Related Documents

RPL-CS-PRO-007: Meter Test Request & Billing Adjustment Procedure

MTR-F-010: Customer Meter Test Request Form

MTR-F-011: Meter Test Report

App-B: Group Acceptance Worksheet

App-C: Standards Certification Register Summary

circuits_master.csv: Service territory circuit reference file

# 20. Revision History

v6.0 (2025-01-08): Updated for 2024-12-31 law snapshot; updated fleet count to 409,950; added AMI HES monitoring section; updated sampling table to internal procedure.

v5.2 (2024-02-05): Annual update; minor corrections to group counts.

# 21. Approval Block

| Role | Name / Title | Signature / Date |
| --- | --- | --- |
| Owner | Gregory Walsh Manager, Meter Shop & Standards Laboratory | Signed: 2025-01-08 |
| Reviewer | Angela Ruiz Director, Metering | Signed: 2025-01-08 |
| Approver | Michael Brennan Vice President, Operations | Signed: 2025-01-08 |